## Sheet1
Theme | Sub-Theme | Document Heading Number | Article / Heading | Table Number | Parameter | Parameter in HVDC | Consultation Proposal | Article Number | Type Applicability | Justification Code | Comment
Frequency | Frequency Ranges for HVDC Systems | 5.1.2.1 | Frequency Ranges for HVDC Systems | 2 | Frequency Ranges | a. 47.5 Hz – 48.5 Hz for a time to specified by each TSO, but not longer than established times for generation and demand. b. 48.5 Hz – 49.0 Hz for a time to be specified by each TSO, but not longer than established times for generation and demand c. 51.0 Hz – 51.5 Hz for a time to be specified by each TSO, but not longer than established times for generation and demand d. 51.5 Hz – 52 Hz for a time to be specified by each TSO but longer than for DC-connected PPMs | a. 47.5 - 48.5 Hz for 90 minutes b. 48.5 - 49.0 Hz for 90 minutes c. 51.0 Hz - 51.5 Hz for 90 minutes d. 51.5 - 52.0 Hz for 60 minutes | 11.1 | HVDC Systems | 2 2 2 1
Frequency | Frequency Ranges for remote-end HVDC converter stations | 5.1.2.2 | Frequency Ranges for remote-end converter stations | 3 | Frequency Ranges | a. 47.5 Hz – 48.5 Hz for a time to specified by each TSO, but not longer than established times for generation and demand. b. 48.5 Hz – 49.0 Hz for a time to be specified by each TSO, but not longer than established times for generation and demand c. 51.0 Hz – 51.5 Hz for a time to be specified by each TSO, but not longer than established times for generation and demand d. 51.5 Hz – 52 Hz for a time to be specified by each TSO but longer than for DC-connected PPMs | a. 47.5 - 48.5 Hz for 90 minutes b. 48.5 - 49.0 Hz for 90 minutes c. 51.0 Hz - 51.5 Hz for 90 minutes d. 51.5 - 52.0 Hz for 60 minutes | 47.1 | Remote-end Converter Stations | 2 2 2 1
Frequency | Wider Frequency Ranges for HVDC Systems | 5.1.2.3 | Wider Frequency Ranges for HVDC Systems | 4 | Wider Frequency ranges, longer minimum times for operation | To be agreed between the TSO and HVDC system owner | Site specific | 11.2 | HVDC Systems | 3
Frequency | Wider Frequency Ranges for HVDC Systems | 5.1.2.4 | Wider Frequency Ranges for Power Park Modules | 5 | Wider Frequency ranges, longer minimum times for operation | To be agreed between the TSO and DC-connected Power Park module owner | Site specific | 39.2(b) | DC-connected PPMs | 3
Frequency | Automatic disconnection of HVDC Systems | 5.1.2.5 | Automatic disconnection of HVDC systems | 6 | Frequency for automatic disconnection | To be specified by the relevant TSO | Site specific | 11.3 | HVDC Systems | 3
Frequency | Automatic disconnection of Power Park Modules | 5.1.2.6 | Automatic disconnection of DC-connected Power Park Modules | 7 | Frequency for automatic disconnection | To be agreed between the TSO and the DC-connected power park module | Site specific | 39.2(c) | DC-connected PPMs | 3
Frequency | Maximum admissible power output below 49 Hz | 5.1.2.7 | Maximum admissible power output below 49 Hz | 8 | Admissible active power reduction from maximum output with following frequency | To be specified by the relevant TSO | Right to specify | 11.4 | HVDC Systems | 3
Frequency | Frequency modes | 5.1.3.1 | Frequency Senstive Mode | 12 | a. Frequency Deadband b. Droop s1 (upward regulation) c. Droop s2 (upward regulation) d. Frequency Response insensitivity | a. Frequency Deadband of 0 -> +/- 500 mHz b. Droop s1 (upward regulation) with a minimum of 0.1 % c. Droop s2 (upward regulation) with a minimum of 0.1 % d. Frequency Response insensitivity Maximum of 30 mHz | a. Frequency Deadband of +/- 15 mHz b. Droop s1 (upward regulation) of 0.1 – 12 %, with a default value of 4 % c. Droop s2 (upward regulation) of 0.1 – 12 %, with a default value of 4 % d. Frequency Response insensitivity Maximum of 15 mHz | 15 | HVDC Systems | 1
Frequency | Frequency modes | 5.1.3.2 | Frequency Control | 13 | a. Need for independent control mode to modulate active power output b. Specify operating principle | a. To be specified by TSO b. To be specified by TSO | a. Site specific b. Site specific | 16.1 | HVDC Systems | 3
Frequency | Frequency modes | 5.1.3.3 | FSM with subject to a fast signal response | 14 | a. Active Power Range (∆P/PMax) b. Frequency response insensitivity (∆f) c. Frequency response insensitivity (∆f/f) d. Frequency Response Deadband e. Droop f. Admissible initial time delay for activation of active power frequency response g. Maximum admissible choice of full activation time h. Capability relating to the duration of provision of full active power frequency response | a. 1.5 -10% (as per the RfG) b. 10 – 30 mHz (as per the RfG) c. 0.02 – 0.06 % (as per the RfG) d. 0 – 500 mHz (as per the RfG) e. 2 – 12 % (as per the RfG) f. Less than 2 seconds (as per the RfG) g. 30 seconds (as per the RfG) h. 20 minutes | a. 60 % in 5 seconds and 100 % in 15 seconds B. 15 mHz* c. 0.03% d. +/- 15 mHz* e. Depends on generation type but 4% is proposed as a default f. 0s - No time delays other than those inherent in the design of the frequency response system g. 5 seconds h. 20 minutes | 39.8 | DC-connected PPMs | 1 / 3
Frequency | Frequency modes | 5.1.3.4 | Limited Frequency Senstive Mode (LFSM) for DC-Connected Power Park Modules | 15 | a. Frequency Threshold b. Droop Settings | a. In accordance with Article 13(2) of Regulation (EU) 2016/631 b. In accordance with Article 13(2) of Regulation (EU) 2016/631 | a. 50. 2 Hz b. Should be capable of operating with a droop in the range of 2- 12 %. The default setting is 4 %. | 39.4 | DC-connected PPMs | 3
Frequency | Frequency modes | 5.1.3.6 | LFSM_U for DC-Connected Power Park Module | 17 | a. Frequency threshold b. Droop Settings | a. In accordance with Article 15(2)(c) of Regulation (EU) 2016/631 b. In accordance with Article 15(2)(c) of Regulation (EU) 2016/631 | a. 49.5 Hz b. Default is 4 % unless otherwise specified by the TSO on a site specific basis | 39.7 | DC-connected PPMs | 3
Frequency | Active Power Controllability | 5.1.4.1 | Active Power Controllability, Control Range and Ramping Rate | 18 | a. Maximum power Step b. Minimum power step c. Minimum active power transmission capacity d. Maximum delay | a. To be specified by TSO b. To be specified by TSO c. To be specified by TSO d. To be specified by TSO | a. To be specified on a case by case basis b. To be specified on a case by case basis c. Not greater than the lesser of 3 % of the HVDC system maximum capacity or 50 MW d. 10 seconds plus the HVDC system ramp rate | 13.1(a)(ii) | HVDC Systems | 1
Frequency | Active Power Controllability | 5.1.4.2 | Modification of transmitted active power | 19 | Modification of transmitted active power | To be specified by the relevant TSO | Site specific | 13.1(b) | HVDC Systems | 3
Frequency | Active Power Controllability | 5.1.4.3 | Fast Active Power Reversal | 20 | Fast Active Power Reversal | To be specified by the relevant TSO | Site specific | 13.1(c) | HVDC Systems | 3
Frequency | Active Power Controllability | 5.1.4.4 | HVDC Systems Automatic Remedial Actions | 21 | Automatic remedial actions | Right to invoke | Right to specify | 13.3 | HVDC Systems | 3
Frequency | Active Power Controllability | 5.1.4.5 | Maximum loss of active power | 22 | maximum loss of active power | To be specified by the relevant TSO | Site specific | 17.1 | HVDC Systems | 3
Frequency | Active Power Controllability | 5.1.4.6 | Maximum loss of actibe power for a HVDC system connecting to control areas | 23 | Maximum loss of actibe power for a HVDC system connecting to control areas | To be agreed between the relevant TSOs | To be agreed between the relevant TSOs on a case by case basis | 17.2 | HVDC Systems which connect two or more control areas | 3
Frequency | Active Power Controllability | 5.1.4.7 | Active power capability for Power Park Modules | 24 | a. The period within which the adjusted active power set point must be reached b. To be specified in accordance with Article 15(2) of the Regulation (EU) 2016/631 | a. To be specified in accordance with Article 15(2) of the Regulation (EU) 2016/631 b. To be specified in accordance with Article 15(2) of the Regulation (EU) 2016/631 | a. The active power set point and the time to achieve this is determined by the TSO, however, following a shutdown, a PPM must commence active power export within 90 secs WFPS schedule 6.11 b. Active power output to be within 3% of set point (based on RC) Time to achieve set point within ±10 seconds of target time. (See WFPS Settings schedule 6.1) | 39.6 | DC-connected power park modules | 1
Frequency | Synthetic Interia | 5.1.5.1 | Synthetic Interia | 25 | Provision of synthetic inertia | To specify or not to specify | Not invoking right to specify | 14.1 | HVDC systems | 1
Frequency | Synthetic Interia | 5.1.5.2 | Synthetic Interia | 26 | Agreement of control system and associated parameters | To be agreed between the relevant TSO and the HVDC system owner | Not invoking right to specify | 14.2 | HVDC Systems | 3
Voltage | Voltage Ranges | 5.2.1.3 | Nominal Operational Voltage Range - Transmission System | 29 | a. For 110 / 275 kV: b. For 400 kV | a. For 110 / 275 kV : 1.12 pu - 1.15 pu (to be specified) b. For 400 kV: 1.05pu - 1.15 pu (unlimited) | a. For 110 / 270 kV: 1.10 pu - 1.12 pu on a case by case basis 1.12 pu - 1.15 pu not allowed b. For 400 kV: 1.05 - 1.15 not allowed | 48.1(a) | Remote-end Converter Stations | N/A
Voltage | Voltage Ranges | 5.2.1.4 | wider operational voltage ranges and longer minimum times for DC-Connected PPMs | 30 | Wider Voltage Ranges and Longer Minimum Times | Not specified | Site Specific | 40.1 (b) | DC-connected PPMs | 3
Voltage | Voltage Ranges | 5.2.1.5 | Wider Voltage Ranges or Longer minimum times for DC-connected power park modules | 31 | Wider Voltage Ranges and Longer Minimum Times | Not specified | Site Specific | 48.1(b) | DC-connected PPMs | 3
Voltage | Automatic disconnection due to voltage level for HVDC Systems | 5.2.1.6.1 | Automatic disconnection due to voltage level for HVDC Converter stations | 32 | a. Minimum Voltage below which Module will automatic disconnect b. Maximum Voltage above which Module will automatic disconnect | a. Not specified b. Not specified | a. Not allowed b. Not allowed | 18.3 | HVDC converter stations | 3
Voltage | Automatic disconnection due to voltage level for Power Park Modules | 5.2.1.6.2 | Automatic disconnection due to voltage level for DC-Connected Power Park Modules | 33 | a. Minimum Voltage below which Module will automatic disconnect b. Maximum Voltage above which Module will automatic disconnect | a. Not specified b. Not specified | a. Not allowed b. Not allowed | 40.1(c) | DC-connected power park modules | 3
Voltage | Reactive Power Capability | 5.2.2.1.1 | Reactive Power Capability at maximum Capacity: U-Q/Pmax Profiles | 34 | a. For 110 kV to 300 kV: Umin Umax Qmin/Pmax (lead) Qmax/Pmax (lag) b. For 300 kV to 400 kV: Umin Umax Qmin/Pmax (lead) Qmax/Pmax (lag) | a. For 110 kV to 300 kV: Umin 0.85pu Umax 1.15 pu Qmin/Pmax (lead) -0.5pu Qmax/Pmax (lag) 0.65 b. For 300 kV to 400 kV: Umin 0.85pu Umax 1.15 pu Qmin/Pmax (lead) -0.5pu Qmax/Pmax (lag) 0.65 | a. For 110 kV to 300 kV: Umin 0.9pu Umax 1.118 pu Qmin/Pmax (lead) -0.33pu Qmax/Pmax (lag) 0.33 b. For 300 kV to 400 kV: Umin 0.9pu Umax 1.05 pu Qmin/Pmax (lead) -0.33pu Qmax/Pmax (lag) 0.33 | 20.1 | HVDC converter stations | 2
Voltage | Reactive Power Capability | 5.2.2.1.2 | Time to achieve target value within P-Q/Pmax Profile | 35 | Time to achieve target | Not specified | Without undue delay but at least within 120 seconds | 20.3 | HVDC converter stations | 1
Voltage | Reactive Power Capability | 5.2.2.1.3 | Reactive Power Capability below Maximum Capacity:P-Q/Pmax Profiles | 36 | a. For 110 kV to 300 kV: Pmic Pmec Qmin/Pmax (lead) Qmin/Pmax (lag) b. For 300 kV to 400 kV: Pmic Pmec Qmin/Pmax (lead) Qmin/Pmax (lag) | a. For 110 kV to 300 kV: Pmic 1.0 pu Pmec 1.0 pu Qmin/Pmax (lead) -0.5 ou Qmin/Pmax (lag) 0.65 pu b. For 300 kV to 400 kV: Pmic 1.0 pu Pmec 1.0 pu Qmin/Pmax (lead) -0.5 pu Qmin/Pmax (lag) 0.65 pu | a. For 110 kV to 300 kV: Pmic 1.0 pu Pmec 1.0 pu Qmin/Pmax (lead) -0.33 ou Qmin/Pmax (lag) 0.33 pu b. For 300 kV to 400 kV: Pmic 1.0 pu Pmec 1.0 pu Qmin/Pmax (lead) -0.33 pu Qmin/Pmax (lag) 0.33 pu | 20.4 | HVDC converter stations | 1
Voltage | Reactive Power Capability | 5.2.2.1.4 | Reactive Power Capability below Maximum Capacity:P-Q/Pmax Profiles | 37 | a. For 110 kV to 300 kV: Umin Umax Qmin/Pmax(lead) Qmin/Pmax(lag) b. For 300 kV to 400 kV: Umin Umax Qmin/Pmax(lead) Qmin/Pmax(lag) | a. For 110 kV to 300 kV: Umin 0.85 pu Umax 1.15 pu Qmin/Pmax(lead) -0.5 pu Qmin/Pmax(lag) 0.65 pu b. For 300 kV to 400 kV: Umin 0.85 pu Umax 1.15 pu Qmin/Pmax(lead) -0.5 pu Qmin/Pmax(lag) 0.65 pu | a. For 110 kV to 300 kV: Umin 0.9 pu Umax 1.118 pu Qmin/Pmax(lead) -0.33 pu Qmin/Pmax(lag) 0.33 pu b. For 300 kV to 400 kV: Umin 0.85 pu Umax 1.05 pu Qmin/Pmax(lead) -0.33 pu Qmin/Pmax(lag) 0.33 pu | 40.2(b)(i) | DC-connected power park modules | 3
Voltage | Reactive Power Capability | 5.2.2.1.5 | Reactive Power Capability below Maximum Capacity:P-Q/Pmax Profiles | 38 | a. For 110 kV to 300 kV: Umin Umax Qmin/Pmax(lead) Qmin/Pmax(lag) b. For 300 kV to 400 kV: Umin Umax Qmin/Pmax(lead) Qmin/Pmax(lag) | a. For 110 kV to 300 kV: Umin 0.85 pu Umax 1.15 pu Qmin/Pmax(lead) -0.5 pu Qmin/Pmax(lag) 0.65 pu b. For 300 kV to 400 kV: Umin 0.85 pu Umax 1.15 pu Qmin/Pmax(lead) -0.5 pu Qmin/Pmax(lag) 0.65 pu | a. For 110 kV to 300 kV: Umin 0.9 pu Umax 1.118 pu Qmin/Pmax(lead) -0.33 pu Qmin/Pmax(lag) 0.33 pu b. For 300 kV to 400 kV: Umin 0.85 pu Umax 1.05 pu Qmin/Pmax(lead) -0.33 pu Qmin/Pmax(lag) 0.33 pu | 48.2(a) and (b) | HVDC converter stations | 3
Voltage | Reactive Power Mode | 5.2.2.2.1 | Standard Reactive Power Control Mode for HVDC Converter Stations | 39 | a. Voltage b. Reactive Power c. Power Factor | a. Not specified b. Not specified c. Not specified | a. Invoke the right to specify b. Invoke the right to specify c. Invoke the right to specify | 22.1 | HVDC converter stations | 1 / 3
Voltage | Reactive Power Mode | 5.2.2.2.2 | Customised Reactive Power Control Mode for HVDC Converter Stations | 40 | Customised control mode | Not specified | Site specific | 22.2 | HVDC converter stations | 3
Voltage | Reactive Power Mode | 5.2.2.2.3 | Voltage Control Mode | 41 | a. Voltage set point b. Steps to adjusted deadband c. t1 = time within which 90% of the change in reactive power is reached d. t2 = time within which 100% of the change in reactive power is reached e. Steady-State Tolerance f. Specification of slope (range and step) | a. Not specified b. Not specified c. 0,1 – 10 sec d. 1 – 60 sec e. Not specified f. Not specified. | a. Continuous b. Site specific c. 1 sec d. 5 sec e. 5% f. Site specific | 22.3 | HVDC converter stations | 3
Voltage | Reactive Power Mode | 5.2.2.2.4 | Reactive Power Control Mode | 42 | a. Maximum Reactive Power Range b. Accuracy of reactive Power | a. Not specifed b. Not specified | a. Site Specific b. 5% | 22.4 | HVDC Systems | 3
Voltage | Reactive Power Mode | 5.2.2.2.5 | Power Factor Control Mode | 43 | a. Maximum allowed step Change in Power Factor b. Maximum set point steps | a. Not specifed b. Not specified | a. Site specific b. 0.01 pu (Power Factor) | 22.5 | HVDC converter stations | 3
Voltage | Reactive Power Mode | 5.2.2.2.6 | Equipment to select control modes remotely | 44 | Equipment | Not specified | Site specific | 22.6 | HVDC converter stations | 3
Voltage | Reactive power exchanged with Network | 5.2.3.1 | Reactive Power Exchanged with the network | 45 | Maximum reactive Power Range | Not specified | Site specific | 21.1 | HVDC converter stations | 3
Voltage | Reactive power exchanged with Network | 5.2.3.2 | Maximum Tolerable Voltage Steps for Reactive Power Variation | 46 | Maximum Tolerable Voltage Step | Not Specified | As per TSSPS | 21.2 | HVDC converter stations | 3
Voltage | Reactive Power Consumptiopn of extra high voltage lines | 5.2.4.1 | Supplementary reactive power requirements | 47 | Right to specify supplementary reactive power requirements when the connection point is remote | To specify or not to specify | TSOs reserve the right to specify | 40.2(b)(ii) | DC-connected PPMs | 3
Voltage | Priority given to Active or Reactive Power | 5.2.5.1 | Priority given to Active or Reactive Power Contribution for HVDC Systems | 48 | Prioritisation requirements during FRT | Active/reactive | Active | 23 | HVDC Systems | 3
Voltage | Priority given to Active or Reactive Power | 5.2.5.2 | Priority given to Active or Reactive Power Contribution for DC-connected Power Park Modules | 49 | Prioritisation requirements during FRT | Active/reactive | Active | 40.3 | DC-connected PPMs | 3
Voltage | Short-circuit requirements | 5.2.6.1 | Short-circuit - Fast Fault current Injection for Symmetrical and Assymmetrical faults | 50 | a. Voltage threshold for fast fault current injection b. End of the voltage deviation c. the characteristics of the fast fault current, including the time domain for measuring the voltage deviation and fast fault current d. the timing and accuracy of the fast fault current, which may include several stages during a fault and after its clearance | a. Not specified b. Not specified c. Not specified d. Not specified | a. During voltage dips i.e. when the voltage is below 0.9 pu b. Once the voltage has recovered to within normal operating voltage range c. Reactive current should be provided for the duration of the voltage deviation within the rating of the PPM d. Rise Time no greater than 100ms and a Settling Time no greater than 300ms. | 19.2 and 19.3 | HVDC Systems | 3
Voltage | Fault - Ride - Through | 5.2.7.1 | Fault Ride Through Capability for HVDC Converter Stations | 51 | a. Uret b. tclear c. Urec1 d. trec1 e. Urec2 f. trec2 | a. Uret 0.00 - 0.3 pu b. tclear 0.14 - 0.25 s c. Urec1 0.25 - 0.85 pu d. trec1 1.5 - 2.5 s e. Urec2 0.85 - 0.9 pu f. trec2 trec1 - 10.0 s | a. Uret 0.00 b. tclear 0.15 s c. Urec1 0.85 pu d. trec1 2.5 s e. Urec2 0.9 pu f. trec2 10.0 s | 25.1 | HVDC converter stations | 2
Voltage | Fault - Ride - Through | 5.2.7.2 | Voltage level the HVDC Converter Station Blocks | 52 | Ublock | Not specified | Site specific | 25.4 | HVDC Systems | 3
Voltage | Fault - Ride - Through | 5.2.7.3 | Fault ride through capability in case of asymmetrical faults | 53 | a. Uret b. tclear c. Urec1 d. trec1 e. Urec2 f. Trec2 | a. Uret 0.00 - 0.3 pu b. tclear 0.14 - 0.25 s c. Urec1 0.25 - 0.85 pu d. trec1 1.5 - 2.5 s e. Urec2 0.85 - 0.9 pu f. trec2 trec1 - 10.0 s | a. Uret 0.0 pu b. tclear 0.15 s c. Urec1 0.85 pu d. trec1 2.5 s e. Urec2 0.9 pu f. trec2 10.0 s | 25.1 | HVDC systems | 2
Voltage | Fault - Ride - Through | 5.2.7.4 | Post Fault Active Power Recovery | 54 | a. When the post-fault active power recovery begins, based on a voltage criterion b. Maximum allowed time for active power recovery c. Magnitude and accuracy for active power recovery | a. Not specified b. Not specified c. Not specified | a. Un < 0.9 pu b. 500 ms / 1s c. 90 % | 26 | HVDC Systems | 3
Power Quality | Power Quality | 5.2.8.1 | Power Quality for HVDC Systems | 55 | Level of voltage distortion or fluctuation of the supply voltage at the connection point | Not specified | ER G5/4-1 Harmonics ER P28 Voltage fluctuation | 24 | HVDC Systems | 3
Power Quality | Power Quality | 5.2.8.2 | Power Quality for DC-connected PPMs | 56 | Voltage and distortion limits | To be specified by the relevant TSO | To be site specific | 44 | DC-connected power park modules | 3
Power Quality | Power Quality | 5.2.8.3 | Power quality for remote-end HVDC converter Stations | 57 | Voltage and distortion limits | To be specified by the relevant TSO | To be site specific | 50 | Remote-end Converter Stations | 3
System Restoration | Power oscillation Damping capability | 5.3.1.1 | Frequency range for oscillations | 58 | Frequency range for oscillations | To be specified by the relevant TSO | To be site specific | 30 | HVDC Systems | 3
System Restoration | Power oscillation Damping capability | 5.3.1.2 | SSTI Study requirements | 59 | Specificatin of extent of SSTI and parameters | To be specified by the TSO in due time for plant design | To be specified on a case by case | 31.2 | HVDC System | 3
System Restoration | Power oscillation Damping capability | 5.3.1.3 | Relevant parties at a connection point | 60 | Identify all parties relevant at the connection point | In due time for plant design | Develop necessary process for the management of data during the implementation phase | 31.3 | All parties relevant at the connection point | 3
System Restoration | Blackstart | 5.3.2.1 | Procurement of Blackstart | 61 | Obtain quote for blackstart | TSO to obtain | Retain the existing services process | 37.1 | HVDC Systems | 1
System Restoration | Blackstart | 5.3.2.2 | Time Frame and voltage limits to energise an AC busbar during blackstart | 62 | Time frame and voltage limits to energise the AC busbar with start, with wider frequency and voltage ranges | In due time for plant design | Site Specific | 37.2 | HVDC system with black start capabilities | 3
System Restoration | Blackstart | 5.3.2.2 | Capacity and availability of black start capability | 63 | Capacity and availability of black start | To be agreed between the TSO and the HVDC system owners | To be agreed on case by case basis | 37.3 | HVDC Systems | 1
Instrumentation, simulation models and protection | Interaction between HVDC Systems and other plant / equipment | 5.4.1.1 | Interaction between HVDC Systems and other plant / equipment | 64 | Specify study required to examine interaction with adjacent equipment | To be specified by TSO | Grid Code Appendix A – Planning Data requirements for Users (other than the DNO) connected to the transmission system only to be modified to include the relevant study requirements and parameters for HVDC System | 29.2 | HVDC Systems | 1
Instrumentation, simulation models and protection | Interaction between HVDC Systems and other plant / equipment | 5.4.1.2 | All relevant parties to studies | 65 | All relevant parties to studies | To be specified by TSO | TSO to develop process for identification of all relevant parties during the implementation phase. | 29.3 | All parties relevant to the studies | 3
Instrumentation, simulation models and protection | Interaction between HVDC Systems and other plant / equipment | 5.4.1.3 | Models and information | 66 | Model / information for in studies | To be specified by the TSO | Case by case basis | 29.4 | HVDC System Owners | 3
Instrumentation, simulation models and protection | Electrical protection schemes and settings | 5.4.2.1 | Specification of electrical protecion schemes and settings | 67 | Specification of protection schemes and settings | To be specified by the TSO | Site specific | 34.1 | HVDC Systems | 1
Instrumentation, simulation models and protection | Electrical protection schemes and settings | 5.4.2.2 | Agreement of electrical protection schemes and settings | 68 | Agreement of electrical schemes and settings | To be agreed between the relevant TSO and the HVDC system owner | Necessary process to be developed during implementation phase. | 34.3 | HVDC Systems | 3
Instrumentation, simulation models and protection | Electrical protection schemes and settings | 5.4.2.3 | Agreement of Control Schemes, including necessary settings | 69 | Control scheme, including settings to be agreed between the relevant TSO and HVDC system owner. | To be agreed between the relevant TSO and the HVDC system owner | It will be necessary to develop a process during the implementation phase. | 35.1 | HVDC Systems | 3
Instrumentation, simulation models and protection | Electrical protection schemes and settings | 5.4.2.4 | Priority rating of protection and control for HVDC Systems | 70 | Priority rating of protection and control for HVDC systems | Change to priority order of protection and control | Process to be developed during implementation phase. | 35.3 | HVDC Systems | 3
Instrumentation, simulation models and protection | Electrical protection schemes and settings | 5.4.2.5 | Changes to protection and control schemes and settings | 71 | Changes to the control modes of HVDC Systems | Changes to the control modes of HVDC Systems, if required by the TSO | Process to be developed during the implementation phase | 36.1 | HVDC Systems | 3
Instrumentation, simulation models and protection | Electrical protection schemes and settings | 5.4.2.6 | Coordination and agreement of changes to schemes and settings of HVDC System Control Modes | 72 | Coordination and agreement of changes | Coordination and agreement between the TSO and HVDC owner for changes to the schemes or settings of parameters of the different control modes and protection of the HVDC system, including the necessary procedure | Process to be developed during the implementation phase | 36.2 | HVDC Systems | 3
Instrumentation, simulation models and protection | Electrical protection schemes and settings | 5.4.2.7 | Equipment specification for remote control of control modes and set points | 73 | Equipment specification to enable remote control of control modes and set points | To be specified by the relevant system operator | Site specific | 36.3 | HVDC systems | 1
Instrumentation, simulation models and protection | Electrical protection schemes and settings | 5.4.2.8 | Provision of protection requirements | 74 | Provision of protection requirements | To be agreed with the RSO, in coordination with the TSO | Site specific | 43.1 | DC-Connected power Park modules | 1
Instrumentation, simulation models and protection | Network Characteristics | 5.4.3.1 | Minimum and maximum short circuit power at the connection point | 75 | Minimum and maximum short circuit power at the connection point | RSO shall make publically available | The TSO also make the short circuit levels for all existing transmission stations publically available as part of the ten year transmission forecast statement | 32.1 | HVDC Systems | 1
Instrumentation, simulation models and protection | Network Characteristics | 5.4.3.2 | Publication of method for calculation of minimum and maximum short circuit power | 76 | Calculation of minimum and maximum short circuit power | RSO to specify and publish method for the calculation of minimum and maximum short circuit power | To be published during implementation phase of the HVDC network code | 42(a) | DC-connected power park modules | 3
Instrumentation, simulation models and protection | Network Characteristics | 5.4.3.3 | Maximum to minimum short circuit range | 77 | Maximum to minimum short circuit range | To be specified by the relevant system operator, in coordination with the relevant TSO. | Site specific | 42(b) | DC-connected power park modules | 3
Instrumentation, simulation models and protection | Network Characteristics | 5.4.3.4 | Provision of network equivalent | 78 | Provision of network equivalent for harmonic studies | In due time for plant design | In due time for plant design | 42(c) | DC-connected power park module | 3
Instrumentation, simulation models and protection | HVDC Robustness | 5.4.4 | HVDC Robustness | 79 | The changes in the system conditions for which the HVDC systems shall remain in stable operation | To be specified by TSO | Frequency and voltage requirements as per sections 5.1 and 5.2 above. Short circuit levels will be site specific | 33.1 | HVDC Systems | 2
Instrumentation, simulation models and protection | Power Quality | 5.4.5.1 | voltage and distortion limits | 80 | Voltage and distortion limits | To be specified by the relevant TSO | To be site specific | 44 | DC-connected power park modules | 3
Instrumentation, simulation models and protection | Output signals for DC-connected Power Park Moduels | 5.4.6 | Output signals for DC-connected Power Park Modules | 81 | Output signals | Specify required output signals | Site-specific | 41.2 | DC-connected power park modules | 1
Instrumentation, simulation models and protection | Power Oscillation and damping during the synchronisation of a HVDC converter station | 5.4.7 | Power Oscillation and damping during the synchronisation of a HVDC converter station | 82 | Limits (including transient max. magnitude, duration and measurement window) of any voltage change to steady-state level | Not greater than 5 % of pre-synchronisation voltage | Site specific but not greater than 5 % of pre-synchronisation voltage | 28 | HVDC converter station | 3
Instrumentation, simulation models and protection | Power Oscillation and Damping during the synchronisation of a DC-connected Power Park Module | 5.4.8 | Power Oscillation and Damping during the synchronisation of a DC-connected Power Park Module | 83 | Limits (including transient max. magnitude, duration and measurement window) of any voltage change to steady-state level | Not greater than 5 % of pre-synchronisation voltage | Site specific but not greater than 5 % of pre-synchronisation voltage | 41.1 | HVDC converter station | 3