## Process
Template Signal List for the Provision of DS3 System Services
In order to comply with signalling requirements set out in the "DS3 System Services New Signalling Requirements" publication, a providing unit may be required to provide evidence of compliance in the form of a Wiring Certificate.
Any providing unit with requirements under the "DS3 System Services New Signalling Requirements" publication must request a site specific signal list from the TSO via e-mail to generator_testing@eirgrid.com or generator_testing@soni.ltd.uk.
The TSO shall issue a site specific signal list to the providing unit.
Upon completion of the necessary works, the providing unit shall submit a signed wiring certificate (using the 'Wiring Certificate' tab from the site specific signal list) verifying that all works have been carried out to make the relevant signals available to the TSO at the signalling interface. This will include physical wiring for sites communicating via RTU.

## Version Control
Signal List Version Control
Version | Date | Written by: | Reviewed by: | Approved by: | Description of changes | Change requested by
Note on D3: Administrator: All signal lists circulated to EMS and ESBT for Review before issuance.

## Signal List
Providing Unit Name | NI WFPS Signal List - System Services - Emulated Inertia |  | V1 | 2019-03-26
Digital Output signals (from TSO) to Providing Unit |  | Permanent | 0.5 second pulse | 0.5 second pulse
|  | Common | Disable | Enable / ON
Signal Description | Digital - Control | Signal | Signal | Signal | Comment
Emulated Inertia (Control) Disable | Control |  | 24 V DC |  | Control from TSO to disable Emulated Inertia
Common |  | 0V DC
Emulated Inertia (Control) Enable | Control |  |  | 24 V DC | Control from TSO to enable Emulated Inertia
Digital Input Signals (to TSO) from Providing Unit |  | Permanent | 0.5 second pulse | 0.5 second pulse
|  | Common | Disable / OFF | Enable / ON
Signal Description | Digital - Feedback | Common | Signal | Signal | Comment
Emulated Inertia (Feedback) Disabled | Feedback |  | 24 V DC |  | Feedback from Providing Unit to confirm status of Emulated Inertia
Common |  | 0V DC
Emulated Inertia (Feedback) Enabled | Feedback |  |  | 24 V DC | Feedback from Providing Unit to confirm status of Emulated Inertia
Analogue Input Signals (to TSO) from Providing Unit
Signal Description | Analogue Signal | Signal | Range |  | Comment
Emulated Inertia FFR Availability | Analogue Signal | 0 - 10 mA | 0-XX MW |  | Signal identifies in real-time the available MW of FFR from Emulated Inertia
Emulated Inertia POR Availability | Analogue Signal | 0 - 10 mA | 0-XX MW |  | Signal identifies in real-time the available MW of POR from Emulated Inertia

## Wiring Certificate
Providing Unit Name | NI WFPS Signal List - System Services - Emulated Inertia |  | V1 | 2019-03-26
Digital Output signals (from TSO) to Providing Unit |  | Permanent | 0.5 second pulse | 0.5 second pulse
|  | Common | Open | Close
Signal Description | Digital - Control | Signal | Signal | Signal | Signal in place | Functionality Confirmed
Emulated Inertia (Control) Disable | Control |  | 24 V DC
Common |  | 0V DC
Emulated Inertia (Control) Enable | Control |  |  | 24 V DC
Digital Input Signals (to TSO) from Providing Unit |  | Permanent | 0.5 second pulse | 0.5 second pulse
|  | Common | Disable / OFF | Enable / ON
Signal Description | Digital - Feedback | Common | Signal | Signal | Signal in place | Functionality Confirmed
Frequency Response Mode (Feedback) Disabled | Feedback |  | 24 V DC
Common |  | 0V DC
Frequency Response Mode (Feedback) Enabled | Feedback |  |  | 24 V DC
Analogue Input Signals (to TSO) from Providing Unit
Signal Description | Analogue Signal | Signal | Range |  | Signal in place | Functionality Confirmed
Emulated Inertia FFR Availability | Analogue Signal | 0 - 10 mA | 0-XX MW
Emulated Inertia POR Availability | Analogue Signal | 0 - 10 mA | 0-XX MW
Confirmation provided by: |  | Date: